## Slide 1: WP4.3 “Integration of SSS index into iTesla platform”
Rafael Segundo and Luigi Vanfretti – KTH
Tuesday 17 2014, Stockholm, Sweden

## Slide 2: Improvement of the SSS index
In order of overcome with the integration issues, major changes to the Small-Signal Stability (SSS) function has been done
A summary of the changes are listed below:
  It is assumed time-series with variable time step.
  If input signals lack of oscillation (flat lines), the function will not be executed.
  The window of time to apply sss analysis is automatically selected.
  Analysis of Input signals is based on variance.
  Only Prony approach is available as ringdown method.
  The three layer small-signal-stability index SMI, AMI and GMI is the main output (as before).
An anex to D4.3 of changes is also available.

## Slide 3: Benefits of changes
Easier to use, less input parameters are required.
Automatic selection where the ringdown method is applied.
Simpler internal computations. Pre-filter is based on variance rather than energy.
Lower probability of error, complex techniques to analyze signals have been avoided.
Use of Prony, more robust ringdown method.
Same small-signal stability index (SMI, AMI and GMI) provided.

## Slide 4: Possible drawbacks and limitations
Time-series with fixed time-step
The larger the number of signals provided, the less accurate the results of the index.
One contingency is assumed on each set of time-series. If the time-series have more contingencies, the function might not work.
The contingency is severe and the post-fault time period is short. A severe disturbance has occurred at time tf and the simulation finish straight
Reverse case of previous point. A minor contingency has occurred and the post-fault time period is too long.

## Slide 5: Initial feedback from Quinary of the improved function
Feedback:
” We made a test with your latest index; Network considered is the French one (CIM : 20130115_1845_SN2_FR0). The offline workflow ran on the ovh Linux machine, simulating 8 contingencies ( each but one involving two lines). The new Smallsignal Matlab returned errors for 3 out of 8 simulated”
Actions:
A small bug was spotted.
The bug has been corrected.
The new code has been send back to Quinary.

## Slide 6: Other related activities
I have spent several sessions with student Thibault Vandewoestyne, who is going to spent some months on RTE, explaining in detail the different indexes developed by KTH for iTesla.
The sessions were devoted to deeply explain the theory used in the different indexes and the code of the Matlab functions.